## Calculator
Overhead Line Three-Section Current Protection Setting Calculator (International)
Version 2.0 ¦ Based on GB/T 14285, IEC 60255 & IEEE C37 ¦ NEW: ACSR library & inverse-time curves ¦ Edit YELLOW cells for auto recalculation
[1] INPUT PARAMETERS (edit yellow cells)
System rated voltage U (kV) | 10
System short-circuit capacity Sk (MVA) | 150
Conductor type | LGJ-95
Line length L (km) | 10
Maximum load current IL.max (A) | 300
Section I reliability factor Krel.I | 1.3
Section II reliability factor Krel.II (coordination method) | 1.1
Section II sensitivity requirement Ksen.II (sensitivity method) | 1.3
Section III reliability factor Krel.III | 1.2
Self-starting factor Kst | 1.5
Return factor Kf | 0.85
[2] INTERMEDIATE CALCULATIONS (auto)
Maximum system voltage Um (kV) | 10.5
System impedance Xs (Ohm) | 0.735
Conductor unit resistance r (Ohm/km) | 0.35
Conductor unit reactance x (Ohm/km) | 0.35
Total line impedance ZL (Ohm) | 4.9497
Bus (sending-end) short-circuit current (A) | 8248
End-of-line short-circuit current Ik.end (A) | 1066
[3] THREE-SECTION PROTECTION SETTINGS (auto)
Section | Pickup Current (A) | Time Delay (s) | Setting Principle | Protection Range | Remark
Section I (Instantaneous) | 1386 | 0 | Set above max end-of-line fault current | First 75%-85% of line length | End 15%-25% is dead zone
Section II (Definite-Time) | 1173 | 0.5 | Sensitivity method (Ksen>=1.3) vs coordination, take max | 100% of line length | Covers Section I dead zone
Section III (Time-Delayed) | 635 | 0.9 | Set above maximum load current | 100% of line + adjacent-line backup | Time delay per coordination ladder
[4] SENSITIVITY VERIFICATION (auto)
Verification Item | Formula | Calculated Value | Requirement | Result
Section II end-of-line sensitivity | 0.9091 |  | >= 1.3 | FAIL
Section III end-of-line sensitivity | 1.6794 |  | >= 1.5 | PASS
[5] ENGINEERING RECOMMENDATIONS
1. Settings are based on typical conductor parameters; verify with the ACTUAL substation short-circuit capacity before application.
2. About 80% of overhead faults are transient; configure an auto-recloser (0.3-0.5s) to restore 70%+ transient faults.
3. Three-section protection CANNOT detect single-phase high-impedance faults; add zero-sequence directional or SEF logic.
4. Section I range shrinks under minimum operating conditions; verify sensitivity for the minimum fault scenario.
[6] INVERSE-TIME CURVE COORDINATION (North America / International)
Curve Type | Time Dial (TD) | Pickup Ip (A) | Fault Current If (A) | Operating Time t (s)
IEEE MI | 0.1 | 300 | 1000 | 0.2227
Inverse-time curve constants (t = TD x A / [(If/Ip)^p - 1])
Curve Type | Constant A | Constant B | Exponent p
IEEE MI (Moderately Inverse) | 0.0515 | 0.114 | 0.02
IEEE VI (Very Inverse) | 19.61 | 0 | 2
IEEE EI (Extremely Inverse) | 28.2 | 0 | 2
IEC SI (Standard Inverse) | 0.14 | 0 | 0.02
IEC VI (Very Inverse) | 13.5 | 0 | 1
IEC EI (Extremely Inverse) | 80 | 0 | 2
Note: inverse-time equation t = TD x A / [(If/Ip)^p - 1] (IEEE MI adds constant B=0.114). If/Ip must be >1. Coordinate curve and TD with upstream/downstream protection.

## Conductor Library
Conductor impedance library (Ohm/km): LGJ / JKLYJ (China) + ACSR (International, 60Hz typical spacing)
Conductor Type | Unit Resistance r (Ohm/km) | Unit Reactance x (Ohm/km)
LGJ-35 | 0.85 | 0.38
LGJ-50 | 0.65 | 0.37
LGJ-70 | 0.46 | 0.36
LGJ-95 | 0.35 | 0.35
LGJ-120 | 0.27 | 0.34
LGJ-150 | 0.21 | 0.34
LGJ-185 | 0.18 | 0.33
LGJ-240 | 0.13 | 0.32
JKLYJ-70 | 0.46 | 0.35
JKLYJ-95 | 0.35 | 0.35
JKLYJ-120 | 0.27 | 0.34
JKLYJ-185 | 0.18 | 0.33
ACSR Partridge 266.8 | 0.414 | 0.389
ACSR Ostrich 300 | 0.368 | 0.382
ACSR Tern 336.4 | 0.318 | 0.378
ACSR Hawk 477 | 0.229 | 0.36
ACSR Dove 556.5 | 0.196 | 0.354
ACSR Drake 795 | 0.138 | 0.335
ACSR Cardinal 954 | 0.113 | 0.325
ACSR Falcon 1590 | 0.066 | 0.298
Note: ACSR values based on 60Hz typical equivalent spacing (~1ft); verify with actual tower geometry.

## User Guide
Overhead Line Protection Setting Calculator (International) - User Guide
How to Use
1. Enter system rated voltage, short-circuit capacity, line length and max load current in the YELLOW cells. 2. Select conductor type from the dropdown (LGJ/JKLYJ/ACSR series); impedance is matched automatically. 3. All settings and sensitivity checks recalculate automatically. 4. In [6], select an inverse-time curve and enter TD/Pickup/If to get the operating time.
Setting Principles
Section I: set above max end-of-line fault current (Krel=1.2-1.3), instantaneous (0s). Section II: sensitivity method (end Ksen>=1.3) vs coordination method, take the max, 0.5s. Section III: set above max load current (Krel x Kst / Kf), ladder time delay 0.9s.
International Adaptation
1. ACSR library based on 60Hz typical spacing (~1ft equivalent); verify with actual tower geometry. 2. Inverse-time curves support IEEE C37.112 (MI/VI/EI) and IEC 60255 (SI/VI/EI) families. 3. Voltage input supports 12.47/13.8/33/34.5kV international distribution voltages.
Engineering Notes
1. Always replace the default 150MVA with the ACTUAL substation short-circuit capacity. 2. Re-check Section I range and sensitivity under minimum operating conditions. 3. Single-phase grounding faults require separate zero-sequence / SEF protection.
References
GB/T 14285 - Technical Code for Relaying Protection and Security Automatic Equipment IEC 60255-151 / IEEE C37.112 - Inverse-time characteristics SJTU/XJTU - Power System Protection courseware